PRE-MAINTENANCE REPORT OF THE SATATION LOCATED RUTSIRO AND RUBAVU DISRICT

- INTRODUCTION

This report presents the initial findings on the automatic weather stations located in Rutsiro and Rubavvu Districts. Therefore, technicians are advised to take these observations into account when planning maintenance activities. The report is based on data collected from July 1st, 2025, to October 10th, 2025 on Rutsiro while from July 1st, 2025, to October 29th, 2025 on Rubavu district.

- FINDINGS

  - RUTSIRO DISTRICT

- BUGARURA AWS

- Reporting status: Since 08/102025 do not report.

- Rain: from 2025-10-01 00:45:00 started to rerecords suspected rainfall (from 01/10/2025 to 08/10/2025 records total rainfall of 2015.2mm).

- Wind direction data: have a decimal point.

- Missing data: 12 days, 14 hours, 35 minutes (check the details in provided excel file).

- NYABIRASI AWS

- Reporting status: up to date

- Air temperature data: Are not available.

- Battery data: Varying between 0.2V and 1.3V (but it reports consistency)

- Missing data: 12 days, 14 hours, 35 minutes (check the details in provided excel file).

- ARGs

| SN | Station | Last communication |
| --- | --- | --- |
| 1 | Mushubati | 19/07/2025 |
| 2 | Ruhango | Up to date |
| 3 | Kivumu | Up to date |

  - RUBAVU DISTRICT

- TAMIRA AWS

- Reporting status: up to date

- Evaporation: suspected values (Same time gave negative values)

- Battery data: Drops below 12 V.

- Missing data: 58 days, 18 hours, 30 minutes, does not report during night (check the details in provided excel file).

- MUHUNGWE AWS

- Reporting status: up to date

- Evaporation: suspected values

- Wind direction: Varies between 110 and 1710.

- Battery data: Always reads 0V, but it reports.

- Missing data: 15 days, 23 hours, 30 minutes (check the details in provided excel file).

- Soil moisture and temperature: at all depths no data available.

- GISENYI AWS

- Reporting status: since 14/07/2025 do not report.

- Wind Speed: Suspected (always is greater than 0.1 m/s).

- Humidity: values have one decimal place

- Soil moisture and temperature: Except at 10 Cm other depths (20 cm,50 Cm and 100 Cm) data are not available.

- ARGs

| SN | Station | Last communication |
| --- | --- | --- |
| 1 | Rugerero | Up to date |
| 2 | Cyanzarwe | Up to date |
| 3 | Busasamana | 08/12/2024 |
| 4 | Kanzenze | 17/08/2025 |

Cyanzarwe and Rugerera from 1/07/2025 up to 29/10/2025 records total rainfall of 430.mm and 420.2 mm respectively, this is suspected due to comparing to all the manual rain gauge located in same district record the rainfall that is between 100mm and 120mm.

Prepared by:

Christian Bikorimana

Ag.Data Quality Control Officer